{"text_format":"1","workbook":"xlsx","n_sheets":3,"sheets":["Tabelle1","Tabelle2","Tabelle3"],"not_rendered":{"charts":0,"images":8,"macros":1,"external_links":0,"defined_names":2,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Tabelle1","index":0,"n_rows":58,"n_cols":28,"rows_kept":58,"cut":false,"hidden":false,"merged":[[46,5,46,6],[23,20,23,21],[24,20,24,21],[23,4,23,5],[24,4,24,5],[44,20,44,21],[45,20,45,21],[46,20,46,21],[44,11,44,12],[35,4,35,5],[35,8,35,9],[39,16,39,17],[44,13,44,14],[36,8,36,9],[36,11,36,12],[45,5,45,6],[23,2,23,3],[23,12,23,13],[14,12,14,13],[39,4,39,5],[39,8,39,9],[15,20,15,21],[16,20,16,21],[17,20,17,21],[18,20,18,21],[7,16,7,22],[8,16,8,22],[9,16,9,22],[10,16,10,22],[14,20,14,21],[35,18,35,19],[35,11,35,12],[35,21,35,22],[35,14,35,15],[34,4,34,5],[39,18,39,19],[39,14,39,15],[38,11,38,12],[39,21,39,22],[39,11,39,12]]}
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,false]
[null,null,null,null,null,null,null,null,null,null,null,"Association pour l'eau, le gaz et la chaleur ",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,false]
[null,null,null,null,null,null,null,null,null,null,null,"Associazione per l'acqua, il gas e il calore ",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,false]
[null,null,null,null,null,null,null,null,null,null,null,"Fachverband für Wasser, Gas und Wärme ",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,false]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,false]
["Rohrweitenbestimmung Hausanschlussleitung > 600 LU",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,false]
["Bitte füllen Sie die grau hinterlegten Felder aus",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,false]
["Wasserversorgung:"]
["Objekt:"]
["Strasse, Nr:"]
["PLZ, Ort:"]
[]
["1  Bestimmung des Durchflusses"]
[]
["Summe loading units:",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,null,"LU"]
["QD LU",null,"Gleichzeitigkeit Wohngebäude",null,null,null,null,null,null,"(Σ LU x 0.1)0.353 x 0.459",null,null,null,null,null,null,null,null,null,null,{"$f":"(U15*0.1)^0.353*0.459","v":0},null,"l/s"]
["QD Spez.",null,"höhere Gleichzeitigkeit, Dauerentnahme, Spitzenentnahme",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"l/s"]
["QD Total",null,"Total Spitzendurchfluss",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"U16+U17","v":0},null,"l/s"]
["QD Total",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"U18/1000","v":0},null,"m3/s"]
[]
[]
["2  Vorbestimmung der Rohrweite"]
[]
["ID     =",null,"QD Total",null,{"$f":"U19","v":0},null,"m3/s","x",4,null,null,null,null,null,null,null,null,null,null,null,{"$f":"SQRT((E24*I24)/(E25*3.141592654))","v":0},null,"m"]
[null,null,null,"v",2,null,"m/s","x","π",null,null,null,null,null,null,null,null,null,null,null,{"$f":"U24*1000","v":0},null,"mm"]
[]
["ID",null,"rechnerischer Rohrinnendurchmesser, in m"]
["v",null,"maximale rechnerische Geschwindigkeit, in m/s"]
["π",null,"Verhältniszahl 1/2 Kreisumfang zu Radius, 3.1416"]
[]
["Wahl Anschlussleitung ausserhalb Gebäude in Polyethylen PE 100, SDR 11:"]
["Bitte Auswahlkästchen anklicken"]
[]
[]
[null,"40x3.7",null,null,"50x4.6",null,null,null,"63x5.8",null,null,"75x6.8",null,null,null,"90x8.2",null,null,"110x10.0",null,null,"125x11.4"]
[null,32.6,null,null,40.799999999999997,null,null,null,51.4,null,null,61.4,null,null,73.599999999999994,null,null,null,90,null,null,102.2]
[]
["Anschlussleitung innerhalb Gebäude in rostbeständigem Stahl 1.4401 / 1.4521:"]
[null,"35x1.5",null,null,"42x1.5",null,null,null,"54x1.5",null,null,"64x2.0",null,null,"76.1x2.0",null,null,null,"89.9x2.0",null,null,"108x2.0"]
[null,32,null,null,39,null,null,null,51,null,null,60,null,null,72.099999999999994,null,null,null,85.9,null,null,104]
[]
[]
["3  Druckvelustberechnung "]
[]
["Δp  =  λ",null,0.02,"x","l",null,"m + FZ 40%",null,null,"x","ρ",999.7,null,"kg/m3  x",null,"v2",{"$f":"IF(ISERROR((U19*4)/(F46^2*3.141592654)),\"\",(U19*4)/(F46^2*3.141592654))","v":""},"m/s  =",null,null,{"$f":"IF(ISERROR((C45*F45*1.4*L45*Q45^2)/(F46*P46)),\" \",((C45*F45*1.4*L45*Q45^2)/(F46*P46)))","v":" "},null,"Pa"]
[null,null,null,null,"ID",{"$f":"IF(AB1=TRUE,B40/1000,IF(AB2=TRUE,E40/1000,IF(AB3=TRUE,I40/1000,IF(AB4=TRUE,L40/1000,IF(AB5=TRUE,O40/1000,IF(AB6=TRUE,S40/1000,IF(AB7=TRUE,V36/1000,\"\")))))))","v":""},null,"m",null,null,null,null,null,null,null,2,null,null,null,null,{"$f":"IF(ISERROR(U45/1000),\" \",U45/1000)","v":" "},null,"kPa"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"IF(ISERROR(U45/100000),\"\",U45/100000)","v":""},null,"bar"]
[]
["λ","Rohrreibungszahl (Temperatur, Geschwindigkeit und Durchmesser berücksichtigender Durchschnittswert)  "]
["l","Gesamtrohrlänge ausserhalb und innerhalb vom Gebäude, in m"]
["FZ","Formteilzuschlag, in % "]
["ρ","Dichte von Wasser, in kg/m3"]
["v","rechnerische Geschwindigkeit, in m/s"]
[]
["Maximal zulässiger Druckverlust gemäss SVGW Richtlinie W3, 40 kPa (0.4 bar)"]
[]
["SVGW, Grütlistrasse 44, Postfach, 8027 Zürich"]
["Telefon 044/288 33 33, Fax 044/202 16 33, www.svgw.ch"]

{"sheet":"Tabelle2","index":1,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}

{"sheet":"Tabelle3","index":2,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}